## Parameter setting address area
system parameters address area: 03H read, 10H, 06H write function code, low address is high byte data.
data address | data item name | Read/Write | data range | default | type of data | unit
0BH | meter type | R |  | 00 A2
110H | communication address | R/W | High byte invalid, 0, address range 1-247, 0 broadcast address | 1 | WORD
111H | communication baut rate | R/W | High byte invalid, 0, 1=1200,2=2400,3=4800,4=9600 | 4－9600 | WORD
112H | display setup | R/W | display page： bit0:active energy bit1：reactive energy ：bit2：voltage Bit3：current bit4：active power bit5：reactive power bit6：Apparent power Bit7：power factor；measure mode BIT0:1active and reactive measurement、0 active forward and reverse measurement | FF，01 | WORD
113H | display setup | R/W | display digit：00： 6+0； 01:5+1； 02:4+2；turning display time：0~10S | 02，05 | WORD
114H | display setup | R/W | tariff setup：00：now allowed，01：allowed；Selection of pulse output type 00：active，01：reactive，02：second impulse | 01，,0 | WORD
11CH | CT ratio | R/W
118H | constant | R/W | 100 1000 2000 | 1000
system parameters address area: 03H read, 10H, 06H write function code, low address is high byte data.
data address | data item name | Read/Write | data range | default | type of data | unit
8100H | 1 time period starting time: time 、minute | R/W | 0-23、0-59 | 07、00 | WORD | 时、分
8101H | First period belongs to the rate of 1: sharp 2: peak 3: Valley 4: flat | R/W | 0-4 | 2 | WORD
8102H | 2 time period starting time: time 、minute | R/W | 0-23、0-59 | 22、00 | WORD | 时、分
8103H | second period belongs to the rate of 1: sharp 2: peak 3: Valley 4: flat | R/W | 0-4 | 3 | WORD
8104H | 3 time period starting time: time 、minute | R/W | 0-23、0-59 | 00、00 | WORD | 时、分
8105H | third period belongs to the rate of 1: sharp 2: peak 3: Valley 4: flat | R/W | 0-4 | 0 | WORD
8106H | 4 time period starting time: time 、minute | R/W | 0-23、0-59 | 00、00 | WORD | 时、分
8107H | Fourth period belongs to the rate of 1: sharp 2: peak 3: Valley 4: flat | R/W | 0-4 | 0 | WORD
8108H | 5 time period starting time: time 、minute | R/W | 0-23、0-59 | 00、00 | WORD | 时、分
8109H | Five period belongs to the rate of 1: sharp 2: peak 3: Valley 4: flat | R/W | 0-4 | 0 | WORD
810AH | 6 time period starting time: time 、minute | R/W | 0-23、0-59 | 00、00 | WORD | 时、分
810BH | six period belongs to the rate of 1: sharp 2: peak 3: Valley 4: flat | R/W | 0-4 | 0 | WORD
810CH | 7 time period starting time: time 、minute | R/W | 0-23、0-59 | 00、00 | WORD | 时、分
810DH | seven period belongs to the rate of 1: sharp 2: peak 3: Valley 4: flat | R/W | 0-4 | 0 | WORD
81OEH | 8 time period starting time: time 、minute | R/W | 0-23、0-59 | 00、00 | WORD | 时、分
810FH | eight period belongs to the rate of 1: sharp 2: peak 3: Valley 4: flat | R/W | 0-4 | 0 | WORD
8110H | Weekend start time: time 、minutes | R/W | 0-23、0-59 | 00、00 | WORD | 时、分
~
811FH
8130H | holiday start time: time and minutes | R/W | 0-23、0-59 | 00、00 | WORD | 时、分
~
813FH
8140H | holiday form *100 |  | MMDD
system parameters address area: 03H read, 10H, 06H write function code, low address is high byte data.
data address | data item name | Read/Write | data range | default | type of data | unit
8120H | system year、month | R/W | 00-99、1-12 | present time | WORD | year month
#N/A | system date、time | R/W | 1-31、0-23 |  | WORD | date, time
#N/A | system min、second | R/W | 0-59、0-59 |  | WORD | min, second

## Real time data address area
Real time data area address 9000H-9FFFH, reserved enough addresses.
Modbus RTU，16 Decimal, word mode, N81, default baud rate 9600
system parameters address area: 03H read, low address is high byte data.
| data address | data item name | Read/Write | data range | type of data | unit | singe phase
| 130H | frequency F | R | 4500～6500 | UINT | 0.01Hz | ■
| 131H | phase voltage V1 | R |  | UINT | 0.01V | ■
| 132H | phase voltage V2 | R |  | UINT | 0.01V
| 133H | phase voltage V3 | R |  | UINT | 0.01V
| 139H-13AH | phase current I1 | R |  | UINT | 0.001A | ■
| 13BH-13CH | phase current I2 | R |  | UINT | 0.001A
| 13DH-13EH | phase current I3 | R |  | UINT | 0.001A
| 140h-141H | Split phase active powerP1 | R |  | LONG | 0.001kW | ■
| 142h-143H | Split phase active powerP2 | R |  | LONG | 0.001kW
| 144H-145H | Split phase active powerP3 | R |  | LONG | 0.001kW
| 146H-147H | System active power Psum | R |  | LONG | 0.001kW
| 148H-149H | Split phase reactive power Q1 | R |  | LONG | 0.001kvar | ■
| 14AH-14BH | Split phase reactive power Q2 | R |  | LONG | 0.001kvar
| 14CH-14DH | Split phase reactive power Q3 | R |  | LONG | 0.001kvar
| 14EH-14FH | system reactive power Qsum | R |  | LONG | 0.001kvar
| 150H-151H | Split phase Apparent power S1 | R |  | LONG | 0.001kva | ■
| 152H-153H | Split phase Apparent power S2 | R |  | LONG | 0.001kva
| 154H-155H | Split phase Apparent power S3 | R |  | LONG | 0.001kva
| 156H-157H | system Apparent power Ssum | R |  | LONG | 0.001kva
| 158H | Split phase power factor PF1 | R |  | INT | 0.001 | ■
| 159H | Split phase power factor PF2 | R |  | INT | 0.001
| 15AH | Split phase power factor PF3 | R |  | INT | 0.001
| 15BH | system power factor PF | R |  | INT | 0.001

## multirate data address area
multi rate data area address A000H-AFFFH, reserve enough addresses.
Modbus RTU，16 Decimal, word mode, N81, default baud rate 9600
present split time energy 03H read, low address is high byte data.
| data address | data item name | Read/Write | data range | type of data | unit
| A000H | Current total active power | R | 0-99999999 | ULONG | 0.01kwh
|  | (current) active rate 1 electric energy | R | 0-99999999 | ULONG | 0.01kwh
|  | (current) active rate 2 electric energy | R | 0-99999999 | ULONG | 0.01kwh
|  | (current) active rate 3 electric energy | R | 0-99999999 | ULONG | 0.01kwh
|  | (current) active rate 4 electric energy | R | 0-99999999 | ULONG | 0.01kwh
| A00AH-A01DH | reserve
| A01EH | Current total reactive power | R | 0-99999999 | ULONG | 0.01kvarh
|  | (current) reactive rate 1 electric energy | R | 0-99999999 | ULONG | 0.01kvarh
|  | (current) reactive rate 2 electric energy | R | 0-99999999 | ULONG | 0.01kvarh
|  | (current) reactive rate 3 electric energy | R | 0-99999999 | ULONG | 0.01kvarh
|  | (current) reactive rate 4 electric energy | R | 0-99999999 | ULONG | 0.01kvarh
| A030H | last month's demand
A031H
last two month's demand
| 0xff00 | 温度 | R |  |  | °C
| 0xFF01 | 时间偏移量 | R/W |  |  | S/D
| 0xfff0 | 电量 | W