MODBUS Communication Protocol

- Read data:

S:

Functional code              register numbers

01      03      00     01      00      02      CRCL      CRCH

Meter address        register address                16 bits CRC check

R:

Function code

01        03      04      00 00    00 0D         CRCL      CRCH

Meter address         bytes numbers  （energy is 13）（BCD） 16 bits CRC check

- Write address:

S:

Function code            register numbers   New address

01     10        00    00    00    01   02   00      01     CRCL      CRCH

Meter address       register address          bytes numbers                     16 bits CRC check

R:

Function code              register numbers

01        10        00    00     00      01       CRCL      CRCH

Meter address          register address                   16 bits CRC check

- Write base:

S:

Function code     register numbers             data

01   10    00 03   00 02    04            00 BC 6E 4E        CRCL      CRCH

Meter address  register address  bytes numbers （energy is12345678）（BCD） 16 bits CRC check

R:

Function code         register numbers

01    10      00  03    00  02             CRCL      CRCH

Meter address     register address                16 bits CRC check

Write Password

S: 01 10 00 1E 00 02 04 12 34 56 78  CRCL   CRCH

R:00 10 00 1E 00 02 CRCL   CRCH

Password Check

S:01 10 00 20 00 03 06 12 34 56 78 00 01  CRCL   CRCH

R:01 10 00 20 00 03 CRCL   CRCH

00 01 stand for write data enabled while  0000  stand for write data disabled

Baud rate: 4800, 8 data bits, evencheck, 1 start bit, 1 stop bit.

0 can’t be the meter address, but it can be the broadcasting address in order to read any data from the meter.